Section 5: Material Specifications & Installation Standards

## 5.1 Overview

This section outlines materials, performance standards, and installation practices for insulation systems. All materials and assemblies shall comply with CSA, ASTM, and UL standards for safety, efficiency, and durability.

## 5.2 Thermal Properties & Material Selection

Selecting the right insulation material ensures performance under design temperature and service conditions. Common materials include fiberglass, mineral wool, foam glass, elastomeric rubber, and urethane foam.

| Material | Service Temp (°C) | Density (kg/m³) | K-Factor (W/m·K) | R-Value (per inch) |
| --- | --- | --- | --- | --- |
| Fiberglass | -60–450 | 24–96 | 0.036 | 4.3 |
| Mineral Wool | -50–650 | 64–160 | 0.042 | 3.8 |
| Foam Glass | -250–400 | 120 | 0.045 | 3.4 |
| Elastomeric | -55–105 | 70–100 | 0.038 | 4.0 |
| Urethane Foam | -180–120 | 32–64 | 0.028 | 5.0 |

Figure 5-1: K-Factor Comparison Chart [Colour retained]

## 5.3 Insulation Thickness Standards

Insulation thickness varies with pipe size and service temperature. The following are general recommendations.

| Service Temp (°C) | Pipe ≤ 2″ | 2–4″ | >4″ | Material |
| --- | --- | --- | --- | --- |
| 0–100 | 25 mm | 40 mm | 50 mm | Fiberglass |
| 100–200 | 40 mm | 50 mm | 65 mm | Mineral Wool |
| 200–400 | 50 mm | 65 mm | 75 mm | Foam Glass |
| Below 0 | 50 mm | 75 mm | 100 mm | Urethane Foam |

## 5.4 Vapor Barriers & Weather Jacketing

Vapor barriers prevent condensation and corrosion. Weather jacketing protects insulation from mechanical damage and UV exposure.

Aluminum: 0.016–0.024 in thick, outdoor service.

Stainless Steel: for corrosive or high-impact environments.

PVC: economical indoor finish for cold systems.

ASJ (All-Service Jacket): foil-scrim-kraft vapor barrier for indoor use.

Figure 5-2: Common Jacketing Configurations [Colour retained]

## 5.5 Firestopping Standards & Inspection Criteria

Firestopping ensures penetrations maintain rated fire resistance. Only listed and tested systems may be used.

ASTM E814 / UL 1479 – Through-penetration firestop systems.

ASTM E1966 / UL 2079 – Fire-resistance of joint systems.

ASTM E2174 – On-site inspection of installed firestops.

IFC 714 – Identification and labeling requirements.

Checklist:

Verify system identification and UL listing.

Ensure correct annular space and sealant materials.

Confirm visible labeling post-installation.

Figure 5-3: UL Firestop System Example [Colour retained]

## 5.6 Installation Practices & Quality Control

Cut insulation cleanly and square using sharp tools.

Apply adhesives evenly; avoid gaps and drips.

Maintain tolerances: ±3 mm circumference, ±6 mm length.

Record installation data (tag number, material, location).

## 5.7 Testing & Verification

Visual Inspection – confirm continuous coverage and sealed joints.

Adhesion Testing – perform periodic pull tests.

Thermal Testing – reference ASTM C680 for heat-loss calculations.

Label Verification – ensure each penetration has correct UL ID.

## 5.8 QR Video References

| Topic | Suggested Source |
| --- | --- |
| Material Identification | NIA Insulation Materials Training – YouTube |
| Firestop Inspection | International Firestop Council – YouTube |
| Vapor Barrier Application | HVAC Insulation Basics – YouTube |
| Jacket Installation | Sheet Metal Fab Training – YouTube |